HVAC Work Order

Record an HVAC service call with the readings that prove the fix, and the refrigerant handling the law requires you to keep.

✦  Part A — The call and the unit

1. Work order details

| Work order number e.g. HVAC-2026-0412 |  |
| --- | --- |
| Date and time logged |  |
| Logged by |  |
| Priority No cooling or heating / Comfort complaint / Routine / Scheduled |  |
| Building and floor |  |
| Area or zone served |  |
| Reported by and contact |  |
| Response due by |  |

2. Unit identification

| Asset ID |  |
| --- | --- |
| Unit type RTU / Split / Chiller / AHU / FCU / VRF / Heat pump / Boiler |  |
| Make |  |
| Model number |  |
| Serial number |  |
| Nominal capacity e.g. 7.5 tons / 26 kW |  |
| Location on site Roof, plant room, ceiling void — say how to reach it |  |
| Refrigerant type R-410A / R-32 / R-134a / R-454B / Other |  |
| Factory charge on nameplate |  |
| Year installed |  |

3. Complaint and initial condition

| Reported symptom, in the caller's words |  |
| --- | --- |
| Space temperature on arrival |  |
| Setpoint |  |
| Unit running on arrival Yes / No / Short cycling / Locked out |  |
| Fault code displayed |  |
| Occupancy affected Yes / No — how many people or which rooms |  |

✦  Part B — Readings that prove the fix

4. Operating readings, as found and as left

| Reading | Unit | As found | As left | Spec or expected |
| --- | --- | --- | --- | --- |
| Suction pressure | psig | 98 | 118 | 118–124 |
| Suction pressure |  |  |  |  |
| Discharge pressure |  |  |  |  |
| Suction line temp |  |  |  |  |
| Liquid line temp |  |  |  |  |
| Superheat |  |  |  |  |
| Subcooling |  |  |  |  |
| Supply air temp |  |  |  |  |
| Return air temp |  |  |  |  |
| Temperature split |  |  |  |  |
| Compressor amps |  |  |  |  |
| Condenser fan amps |  |  |  |  |
| Blower motor amps |  |  |  |  |
| External static pressure |  |  |  |  |

✦  As found and as left in the same row is the whole point. A single set of readings tells the customer nothing about what you changed.

5. Component checks

| Check | Done | Condition or reading | Action taken | Date |
| --- | --- | --- | --- | --- |
| Air filter — size and condition | ☐ |  |  |  |
| Evaporator coil cleanliness | ☐ |  |  |  |
| Condenser coil cleanliness | ☐ |  |  |  |
| Condensate pan and drain clear | ☐ |  |  |  |
| Belt tension and wear | ☐ |  |  |  |
| Blower wheel clean | ☐ |  |  |  |
| Contactor and relays | ☐ |  |  |  |
| Capacitor microfarads vs rated | ☐ |  |  |  |
| Electrical connections tight | ☐ |  |  |  |
| Thermostat calibration and schedule | ☐ |  |  |  |
| Economiser damper operation | ☐ |  |  |  |
| Safety controls and limits | ☐ |  |  |  |
| Insulation and line-set condition | ☐ |  |  |  |

✦  Filter size belongs in this table, not in someone's memory. It is the single most requested detail on a return visit.

✦  Part C — Refrigerant, parts and labour

6. Refrigerant handling record

| Date | Refrigerant | Recovered (lb/kg) | Added (lb/kg) | Cylinder ID | Leak test method | Result |
| --- | --- | --- | --- | --- | --- | --- |
| 18/09/2026 | R-410A | 0.00 | 2.40 | CYL-7741 | Electronic detector | No leak found |
| Net refrigerant added |  |  |  |  |  |  |

✦  Required record, not a nicety. Every charge and recovery is logged against the unit and the cylinder it came from.

7. Parts fitted

| Part number | Description | Qty | Unit price | Line total | Charge to |
| --- | --- | --- | --- | --- | --- |
| CAP-45-370 | Run capacitor 45µF 370V | 1 | 18.50 | 18.50 | Billable |
| Parts total |  |  |  |  |  |

8. Labour

| Date | Technician | Licence no. | Hours | Rate | Line total |
| --- | --- | --- | --- | --- | --- |
| 18/09/2026 | D. Osei | EPA608-II-4471 | 2.50 | 72.00 | 180.00 |
| Labour total |  |  |  |  |  |

9. Visit total

| Parts total |  |
| --- | --- |
| Labour total |  |
| Refrigerant charge |  |
| Subtotal |  |
| Tax / VAT rate (%) e.g. 20 |  |
| Tax / VAT |  |
| Total for this visit |  |

✦  Part D — Outcome

10. Resolution

| Fault found |  |
| --- | --- |
| Root cause |  |
| Work carried out |  |
| Unit left Fully operational / Operational with limitations / Out of service |  |
| Repair type Permanent / Temporary — return required |  |
| Recommendation Repair again, replace, or change the service interval |  |
| Estimated remaining life |  |
| Follow-up work order raised Yes / No — reference |  |

11. Sign-off

| Technician name |  |
| --- | --- |
| EPA 608 or equivalent certification no. |  |
| Signature |  |
| Customer name and position |  |
| Customer signature |  |
| Date and time |  |

12. Notes