## Preventive Maintenance Work Ord
Preventive Maintenance Work Order
Run a scheduled PM against its task list, record as-found and as-left against specification, and turn every deficiency into a corrective work order before you close it.
✦ Part A — The schedule
1. Work order details
Work order number e.g. PM-2026-0904
PM schedule reference
Date due
Date performed
Days early or late
Trigger Calendar / Running hours / Cycles / Condition / Regulatory
Frequency Weekly / Monthly / Quarterly / Six-monthly / Annual / Other
Planned duration
Assigned to
2. Asset
Asset ID and description
Location
Make and model
Serial number
Criticality A — critical / B — important / C — routine
Meter reading at this PM
Meter reading at last PM
Isolation or permit required Yes / No — reference
✦ Part B — The task list
3. PM task list
Task |  |  |  |  | Done | As found |  | As left | Initial
Visual inspection for damage, leaks and corrosion |  |  |  |  | ☐
Clean unit and surrounding area |  |  |  |  | ☐
Check and record operating readings |  |  |  |  | ☐
Lubricate per schedule |  |  |  |  | ☐
Check belt tension and condition |  |  |  |  | ☐
Check and tighten electrical connections |  |  |  |  | ☐
Check and tighten mechanical fixings |  |  |  |  | ☐
Inspect and replace filters |  |  |  |  | ☐
Check alignment and vibration |  |  |  |  | ☐
Test safety devices and interlocks |  |  |  |  | ☐
Check control settings against specification |  |  |  |  | ☐
Check drainage and condensate paths |  |  |  |  | ☐
Confirm labelling and signage legible |  |  |  |  | ☐
Function test through full operating range |  |  |  |  | ☐
✦ As found and as left in the same row. A PM that only records the final state cannot tell you whether the interval is right.
4. Readings against specification
Measurement |  |  | Unit | Specification |  | As found |  | As left | Pass
Bearing temperature |  |  | °C | < 70 |  | 78 |  | 62 | Y
✦ An out-of-tolerance reading that was corrected is still an out-of-tolerance reading. Record both numbers so the trend survives.
5. Consumables replaced
Item |  |  | Part number |  | Qty | Unit cost |  | Line total | Next due
Panel filter 594×594×48 |  |  | FLT-2424-2 |  | 4 | 9.2 |  | 36.8 | Q1 2027
Consumables total | [7 empty] | 36.8
✦ Part C — Deficiencies and closure
6. Deficiencies found
# | Deficiency |  |  |  | Severity |  | Can it wait | Corrective WO raised | Target date
1 | Coupling guard cracked |  |  |  | Safety |  | No | CWO-2026-1191 | 01/10/2026
✦ A deficiency without a corrective work order number is a deficiency nobody will fix. This column is the whole reason the PM was worth doing.
7. Labour
Date |  | Technician |  |  | Trade |  | Hours | Rate | Line total
01/10/2026 |  | J. Farrow |  |  | Mechanical |  | 1.75 | 58 | 101.5
Labour total | [8 empty] | 101.5
8. PM cost and interval review
Consumables total | [6 empty] | 36.8
Labour total | [6 empty] | 101.5
Total cost of this PM | [6 empty] | 138.3
Planned hours
Actual hours
Hours over or under plan | [6 empty] | 0
Deficiencies found at this PM
Interval recommendation keep, shorten, or lengthen — and why
✦ Zero deficiencies several visits running usually means the interval is too short, not that the asset is perfect. Say so here rather than leaving the schedule untouched by default.
9. Closure
PM completed in full Yes / No — tasks not done and why
Asset returned to service Yes / No — date and time
Isolation removed and tested Yes / No
Records and asset history updated Yes / No
Next PM due — date or meter
Technician name and signature
Verified by and date
10. Notes

## How to use
Preventive Maintenance Work Order
How to use this file
1. Fill the white cells. Grey cells calculate themselves — do not type in them.
2. Work the task list in order and record as found and as left for anything measurable.
3. Enter the specification alongside the reading so a pass or fail is obvious to the next person.
4. Every deficiency needs a corrective work order number before this PM can be closed.
5. Consumables and labour line totals compute from quantity and rate.
6. Enter planned and actual hours; the variance calculates itself and feeds the interval review.
7. Use the Job Log tab if you run a rolling file rather than a document per PM.
Key
White cell with a border | You type here
Grey cell | Calculated — leave it alone
Grey italic row | Worked example showing the expected format
Every field in this workbook also appears in the Word and PDF versions of this template. The Job Log tab is the one addition, for teams who keep a running file rather than a document per job.

## Job Log
WO number | Schedule ref | Asset ID | Due | Performed | Days late | Meter | Planned hrs | Actual hrs | Consumables | Labour | Total cost | Deficiencies | Corrective WOs | Next due
PM-2026-0904 | SCH-AHU-Q | AHU-03 | 28/09/2026 | 01/10/2026 | 3 | 18446 | 1.5 | 1.75 | 36.8 | 101.5 | 138.3 | 1 | 1 | 01/01/2027
Total | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
One row per PM. Compare deficiencies found against interval over time — that is the argument for changing a schedule. The example row is grey italic — overwrite it or delete it.